## Slide 1: Discussion KPI - Quantification Javier Arroyo Berlin Meeting 28/Feb/2018

## Slide 2: Objectives
Fair comparison
Accessibility
Define accurately a set of KPIs to assess control algorithms for BEM.
  Group them into categories
  Choose those that are necessary or nice-to-have for a fair comparison.
  Avoid redundancies.
Unambiguously define their quantification/qualification
  Some can be quantified
  Some use a quality level, e.g. 1 till 5
Discuss on practical issues:
  Solver vs. emulator KPIs
  Dependencies on developer, region or availability of data
  Who should implement the KPI: emulator/solver/docker developers
  Grouping accordingly to the objective function
Conclusions.
  Which to keep? How to calculate them from the emulators?

## Slide 3: Visualization
Comparison to a reference (still to be defined)
Comparison to total population (relative position and range)
E.g. Radar plot Box plot

## Slide 4: Proposed KPIs
ENERGY INDICATORS | COST INDICATORS | COMPUTATION INDICATORS
Achieved energy savings | Development time | Computation time
Energy use | Cost savings | Compilation time
Energy efficiency | Extra hardware costs | Flexibility of supported formulations
Primary energy use | Data requirements | Compactness
ENVIRONMENTAL INDICATORS | Payback period | Usability
CO2 emissions | IEQ INDICATORS | Scaling of computation time
Share of RES | Thermal (dis)comfort | Scalability
Flexibility provided to grid | IAQ (dis)comfort | Robustness/Fault tolerance
 |  | Optimality

## Slide 5: Energy KPIs
Name: Energy Savings
Description: Energy savings achieved when implementing MPC during one year.
Units: kWh/(m2.y)
Quantification: Difference in energy use with respect to a reference controller  What to use as a reference?
Output needed from emulator:
Proposed by: Michael Wetter
Conclusion: we shouldn’t calculate energy savings but energy use instead (see next slide).
CAN BE DROPPED

## Slide 6: Energy KPIs
Name: Energy Use
Description: Energy use in one year of simulation.
Units: kWh/(m2.y)
Quantification: Sum of the energy used by all appliances working on acclimatization for one year.
Output needed from emulator:
Proposed by: Iago
Conclusion: we should calculate this one and split it by application  Heating, cooling, ventilation and lighting (if implemented). Use kWh instead of kWh/m2/y and perform annual tests instead of representative weeks.
TO BE CALCULATED
Notes: Recall! Why kWh?

## Slide 7: Energy KPIs
Name: Energy Efficiency
Description: Seasonal performance.
Units: %
Quantification:
Output needed from emulator:
Proposed by: Iago
Conclusion: Redundant.
CAN BE DROPPED

## Slide 8: Energy KPIs
Name: Primary Energy Use
Description: Seasonal performance.
Units:
Quantification:
Output needed from emulator:
Proposed by: Iago
Conclusion: this is derived from energy use.
CAN BE DROPPED

## Slide 9: Environmental KPIs
Name: CO2 emissions
Description: Estimated CO2 emissions proposed by the solution.
Units: kg CO2/y or ton CO2/y
Quantification:
Output needed from emulator:
Proposed by: Iago
Conclusion: this one certainly needs to be calculated.
TO BE CALCULATED

## Slide 10: Environmental KPIs
Name: Share of RES
Description: estimated used RES from the grid and self-production.
Units: kWh
Quantification:
Output needed from emulator:
Proposed by: Iago
Conclusions: This one is derived from energy use.
CAN BE DROPPED
Notes: Which factors to be used? They depend on the energy mix  table per country?

## Slide 11: Environmental KPIs
Name: Flexibility provided to grid
Description: Some indication of load flexibility provided to grid.
Units:
Quantification:
Output needed from emulator:
Proposed by: Michael Wetter
Conclusion: Need to have further thoughts about this one. Krzysztof will keep us informed about discussions within the Annex 67 where they are already working on a common way to define flexibility.
TO BE CALCULATED

## Slide 12: Cost KPIs
Name: Development time
Description: Human time required for generating MPC controller.
Units: hours.
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusions: this KPI should be quantified qualitatively with different categories of implementation time.
TO BE CALCULATED

## Slide 13: Cost KPIs
Name: Cost savings
Description: Similar to energy savings, but cost depends also on the price signal.
Units: USD/EUR
Quantification: Difference in operational cost with respect to a reference controller  What to use as a reference?
Output needed from emulator:
Proposed by: Krzysztof, Christian
Conclusion: Use cost instead of cost savings. Lump energy use into one cost.
CAN BE DROPPED
Notes: Recall!

## Slide 14: Cost KPIs
Name: Extra hardware costs
Description: In case of additional hardware required for the installation of the MPC.
Units: USD/EUR
Quantification: Sum of the cost of installing any extra-hardware required to get the MPC running (sensors, interfaces to BMS, …).
Output needed from emulator:
Proposed by: Javier
Conclusions: Hard to quantify, still not clear from the discussion.
CAN BE DROPPED
Notes: Recall

## Slide 15: Cost KPIs
Name: Data requirements
Description: cost of gathering data for training grey- and black-box models, or even for calibrating white-box models (if needed).
Units: USD/EUR
Quantification: Cost of installing additional sensors and exciting the building (if needed).
Output needed from emulator:
Proposed by: Javier
Conclusions: this KPI should be quantified qualitatively with different categories of data requirements. 2 types: 1) special excitations, 2) extra sensors or not.
TO BE CALCULATED

## Slide 16: Cost KPIs
Name: Payback period
Description: Period needed to recover the cost of the initial investment.
Units: months
Quantification: (Initial investment)/(monthly cost savings)
Output needed from emulator:
Proposed by: Javier
Conclusion: common cost tables for computing payback period. Very hard to quantify in practice?
TO BE CALCULATED
Notes: Recall!

## Slide 17: Indoor Environmental Quality KPIs
Name: Thermal (dis)comfort
Description: Deviation from allowed comfort bounds.
Units: Kh
Quantification: (Thermal deviation)*time
Output needed from emulator:
Proposed by: Michael
Conclusion: we use thermal discomfort as this one is already adopted by the community. We should calculate it in K*h and maximum K. Two further discussion points: 1) what if the building is unoccupied? 2) How to treat multi-zone?.
TO BE CALCULATED

## Slide 18: Indoor Environmental Quality KPIs
Name: Indoor Air Quality (dis)comfort
Description: Deviation from target specifications about the quality of the air inside the building. Lighting, glare…
Units: concentrations of pollutants.
Quantification: (Operations target) – (Operations achieved)
Output needed from emulator:
Proposed by: Davy
Conclusion: this one is ‘a nice-to-have’.
CAN BE DROPPED

## Slide 19: Computation KPIs
Name: Computation time
Description: Computation time per MPC solution
Units: Seconds
Quantification: time required for an MPC computation  from getting the measurements till deliver optimal solution
Output needed from emulator:
Proposed by: Filip
Conclusion: should be normalised with standard computation benchmark. It is a good indicator for scalability.
TO BE CALCULATED

## Slide 20: Computation KPIs
Name: Compilation time
Description: Computer-time required for generating MPC controller.
Units: Seconds
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: can be part of development time.
CAN BE DROPPED

## Slide 21: Computation KPIs
Name: Flexibility of supported formulations
Description: Type of supported formulations.
Units: NLP/LP/MILP/MINLP/QP/QCQP/...
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: not strongly needed.
CAN BE DROPPED

## Slide 22: Computation KPIs
Name: Compactness
Description: Number of optimisation variables.
Units: Seconds
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: not strongly needed.
CAN BE DROPPED

## Slide 23: Computation KPIs
Name: Usability
Description: The ease of use for the user.
Units:
  GUI used to interface to solver.
  Code-based framework used to interface to solver.
  Direct interface to solver.
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: this one is derived from other indicators like development time.
CAN BE DROPPED

## Slide 24: Computation KPIs
Name: Scaling of computation time
Description: Scaling of computation time with respect to number of states nx, constraints nc, control intervals ni.
Units: O(nx^a), O(nc^b), O(ni^c)
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: not strongly needed.
CAN BE DROPPED

## Slide 25: Computation KPIs
Name: Scalability
Description: Absolute bound for model size in terms of number of states nx, constraints nc, control intervals ni, given a certain computation time and/or memory.
Units: nx, nc, ni
Quantification:
Output needed from emulator:
Proposed by: Filip
Conclusion: not strongly needed.
CAN BE DROPPED

## Slide 26: Computation KPIs
Name: Robustness/Fault tolerance
Description: Ability to deal with uncertainty of input data, possibly missing data or inaccurate models due to changing system characteristics.
Units: Percent of passed (predefined) tests.
Quantification:
Output needed from emulator:
Proposed by: Krysztof, Christian
Conclusion: difficult to quantify/standardize?
CAN BE DROPPED
Notes: Recall!!!

## Slide 27: Computation KPIs
Name: Optimality
Description: Comparison to known optimal solution if possible, or best known solution so far – similar to energy/cost savings but comparative basis. Could apply to constraint violations.
Units: %
Quantification:
Output needed from emulator:
Proposed by: Dave
Conclusion: not strongly needed.
CAN BE DROPPED

## Slide 28: Conclusions
ENERGY INDICATORS | COST INDICATORS | COMPUTATION INDICATORS
Achieved energy savings | Development time | Computation time
Energy use | Cost savings | Compilation time
Energy efficiency | Extra hardware costs | Flexibility of supported formulations
Primary energy use | Data requirements | Compactness
ENVIRONMENTAL INDICATORS | Payback period | Usability
CO2 emissions | IEQ INDICATORS | Scaling of computation time
Share of RES | Thermal discomfort | Scalability
Flexibility provided to grid | IAQ (dis)comfort | Robustness/Fault tolerance
 |  | Optimality
Which indicators to keep?
How to calculate them from the emulators?
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED
TO BE CALCULATED